## Table Modbus
| 31000 | First Register
[5 empty] | EN302 | EN303 | EN304 | EN305 | EN308 | EN309 | EN310 | EN319 | EN306 | EN307 | EN311
| Modbus Register Table for Transmitters (Read Only) - to be suppoorted both as Holding and Input Registers (Code 3 and 4) |  |  |  | Ambient T&H | Ambient T&H / VOC | Ambient T&H / VOC / CO2 | Tx Temp Internal Sensor | Tx Pulse | Tx Pulse (Atex) | Tx Pulse (Fludia) | Tx Contact | Tx Temp Ext PT1000 (2) | Tx Analog 4-20mA | External T&H | Tx Temp Ext PT1000 (1) | Tx Temp Ext PT1000 (1) Ext Power | Tx Temp Ext PT1000 (2) Ext Power | Register
[5 empty] | TX T&H AMB 600-021 | TX VOC/T&H AMB 600-022 | TX CO2/VOC/T&H AMB 600-023 | TX TEMP INS 600-031 | TX PULSE 600-036 | TX PULSE ATEX 600-037 | TX PULSE LED 600-038 | TX CONTACT 600-039 | TX TEMP CONT2 600-232 | TX 4/20 mA 600-035 | TX T&H 600-034 | TX TEMP CONT1 600-032 | TX TEMP CONT1 MP 600-033 | TX TEMP CONT2 MP 600-233
[5 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
| Register Address | Parameter | Bytes | Comment
| 31000 | Num_of_Dev | 2 | Number of Devices in Table | [14 empty] | 31000
| 31001 | Spare | 2 | Spare | [14 empty] | 31001
| 31002 | Spare | 2 | Spare | [14 empty] | 31002
1 | 31003 | DeviceID( Higher word) | 2 | Device ID HO | [14 empty] | 31003 | bar: 0 to 13
| 31004 | DeviceID( Lower word) | 2 | Device ID LO | [14 empty] | 31004 | bar: 0 to 13
| 31005 | Device Type / F/W ver | 2 | Higher Byte Type / Lower Byte Firmware version | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | 31005
| 31006 | Status | 2 | Status (see bit descriptions) | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | 31006
| 31007 | Alarm Status | 2 | Alarm Status (see bit descriptions) | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | 31007
| 31008 | Data(word1) | 2 | Data | Temperature | Temperature | Temperature | Temperature | 0 | 0 | 0 | 0 | Temperature (Ch1) | Analog Value | Temperature | Temperature (Ch1) | Temperature (Ch1) | Temperature (Ch1) | 31008
| 31009 | Data(word2) | 2 | Data | Humidity | Humidity | Humidity | 0 | Ch1 Count HO | Ch1 Count HO | 0 | Ch1 Count HO | Temperature (Ch2) | 0 | Humidity | 0 | 0 | Temperature (Ch2) | 31009
| 31010 | Data(word3) | 2 | Data | 0 | VOC | VOC | 0 | Ch1 Count LO | Ch1 Count LO | 0 | Ch1 Count LO | 0 | 0 | 0 | 0 | 0 | 0 | 31010
| 31011 | Data(word4) | 2 | Data | 0 | 0 | CO2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31011
| 31012 | Data(word5) | 2 | Data | 0 | 0 | 0 | 0 | Ch2 Count HO | Ch2 Count HO | 0 | Ch2 Count HO | 0 | 0 | 0 | 0 | 0 | 0 | 31012
| 31013 | Data(word6) | 2 | Data | 0 | 0 | 0 | 0 | Ch2 Count LO | Ch2 Count LO | 0 | Ch2 Count LO | 0 | 0 | 0 | 0 | 0 | 0 | 31013
| 31014 | Data(word7) | 2 | Data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31014
| 31015 | Data(word8) | 2 | Data | 0 | 0 | 0 | 0 | OC Count HO | OC Count HO | OC Count HO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31015
| 31016 | Data(word9) | 2 | Data | 0 | 0 | 0 | 0 | OC Count LO | OC Count LO | OC Count LO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31016
| 31017 | Spare | 2 | Spare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31017
| 31018 | Spare | 2 | Spare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31018
| 31019 | Spare | 2 | Spare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31019
| 31020 | Tx Counter | 2 | Transmission Counter sent by Tx | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | 31020
| 31021 | RSSI | 2 | Received RSSI value | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | 31021
| 31022 | Timer | 2 | Time since last reading value - increments every 1 min and resets when data received | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | 31022
2 | 31023 | DeviceID( Higher word) | 2 | Device ID HO | [14 empty] | 31023 | bar: 0 to 13
| 31024 | DeviceID( Lower word) | 2 | Device ID LO | [14 empty] | 31024 | bar: 0 to 13
| 31025 | Device Type / F/W ver | 2 | Higher Byte Type / Lower Byte Firmware version | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | 31025
| 31026 | Status | 2 | Status (see bit descriptions) | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | 31026
| 31027 | Alarm Status | 2 | Alarm Status (see bit descriptions) | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | 31027
| 31028 | Data(word1) | 2 | Data | Temperature | Temperature | Temperature | Temperature | 0 | 0 | 0 | 0 | Temperature (Ch1) | Analog Value | Temperature | Temperature (Ch1) | Temperature (Ch1) | Temperature (Ch1) | 31028
| 31029 | Data(word2) | 2 | Data | Humidity | Humidity | Humidity | 0 | Ch1 Count HO | Ch1 Count HO | 0 | Ch1 Count HO | Temperature (Ch2) | 0 | Humidity | 0 | 0 | Temperature (Ch2) | 31029
| 31030 | Data(word3) | 2 | Data | 0 | VOC | VOC | 0 | Ch1 Count LO | Ch1 Count LO | 0 | Ch1 Count LO | 0 | 0 | 0 | 0 | 0 | 0 | 31030
| 31031 | Data(word4) | 2 | Data | 0 | 0 | CO2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31031
| 31032 | Data(word5) | 2 | Data | 0 | 0 | 0 | 0 | Ch2 Count HO | Ch2 Count HO | 0 | Ch2 Count HO | 0 | 0 | 0 | 0 | 0 | 0 | 31032
| 31033 | Data(word6) | 2 | Data | 0 | 0 | 0 | 0 | Ch2 Count LO | Ch2 Count LO | 0 | Ch2 Count LO | 0 | 0 | 0 | 0 | 0 | 0 | 31033
| 31034 | Data(word7) | 2 | Data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31034
| 31035 | Data(word8) | 2 | Data | 0 | 0 | 0 | 0 | OC Count HO | OC Count HO | OC Count HO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31035
| 31036 | Data(word9) | 2 | Data | 0 | 0 | 0 | 0 | OC Count LO | OC Count LO | OC Count LO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31036
| 31037 | Spare | 2 | Spare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31037
| 31038 | Spare | 2 | Spare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31038
| 31039 | Spare | 2 | Spare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31039
| 31040 | Tx Counter | 2 | Transmission Counter sent by Tx | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | 31040
| 31041 | RSSI | 2 | Received RSSI value | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | 31041
| 31042 | Timer | 2 | Time since last reading value - increments every 1 min and resets when data received | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | 31042
3 | 31043 | DeviceID( Higher word) | 2 | Device ID HO | [14 empty] | 31043 | bar: 0 to 13
| 31044 | DeviceID( Lower word) | 2 | Device ID LO | [14 empty] | 31044 | bar: 0 to 13
| 31045 | Device Type / F/W ver | 2 | Higher Byte Type / Lower Byte Firmware version | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | 31045
| 31046 | Status | 2 | Status (see bit descriptions) | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | 31046
| 31047 | Alarm Status | 2 | Alarm Status (see bit descriptions) | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | 31047
| 31048 | Data(word1) | 2 | Data | Temperature | Temperature | Temperature | Temperature | 0 | 0 | 0 | 0 | Temperature (Ch1) | Analog Value | Temperature | Temperature (Ch1) | Temperature (Ch1) | Temperature (Ch1) | 31048
| 31049 | Data(word2) | 2 | Data | Humidity | Humidity | Humidity | 0 | Ch1 Count HO | Ch1 Count HO | 0 | Ch1 Count HO | Temperature (Ch2) | 0 | Humidity | 0 | 0 | Temperature (Ch2) | 31049
| 31050 | Data(word3) | 2 | Data | 0 | VOC | VOC | 0 | Ch1 Count LO | Ch1 Count LO | 0 | Ch1 Count LO | 0 | 0 | 0 | 0 | 0 | 0 | 31050
| 31051 | Data(word4) | 2 | Data | 0 | 0 | CO2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31051
| 31052 | Data(word5) | 2 | Data | 0 | 0 | 0 | 0 | Ch2 Count HO | Ch2 Count HO | 0 | Ch2 Count HO | 0 | 0 | 0 | 0 | 0 | 0 | 31052
| 31053 | Data(word6) | 2 | Data | 0 | 0 | 0 | 0 | Ch2 Count LO | Ch2 Count LO | 0 | Ch2 Count LO | 0 | 0 | 0 | 0 | 0 | 0 | 31053
| 31054 | Data(word7) | 2 | Data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31054
| 31055 | Data(word8) | 2 | Data | 0 | 0 | 0 | 0 | OC Count HO | OC Count HO | OC Count HO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31055
| 31056 | Data(word9) | 2 | Data | 0 | 0 | 0 | 0 | OC Count LO | OC Count LO | OC Count LO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31056
| 31057 | Spare | 2 | Spare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31057
| 31058 | Spare | 2 | Spare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31058
| 31059 | Spare | 2 | Spare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31059
| 31060 | Tx Counter | 2 | Transmission Counter sent by Tx | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | 31060
| 31061 | RSSI | 2 | Received RSSI value | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | 31061
| 31062 | Timer | 2 | Time since last reading value - increments every 1 min and resets when data received | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | 31062
| . |  |  | .
| . |  |  | .
| . |  |  | .
| . |  |  | .
| . |  |  | .
| . |  |  | .
.
32 | 31623 | DeviceID( Higher word) | 2 | Device ID HO | [14 empty] | 31623 | bar: 0 to 13
| 31624 | DeviceID( Lower word) | 2 | Device ID LO | [14 empty] | 31624 | bar: 0 to 13
| 31625 | Device Type / F/W ver | 2 | Higher Byte Type / Lower Byte Firmware version | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | 31625
| 31626 | Status | 2 | Status (see bit descriptions) | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | 31626
| 31627 | Alarm Status | 2 | Alarm Status (see bit descriptions) | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | 31627
| 31628 | Data(word1) | 2 | Data | Temperature | Temperature | Temperature | Temperature | 0 | 0 | 0 | 0 | Temperature (Ch1) | Analog Value | Temperature | Temperature (Ch1) | Temperature (Ch1) | Temperature (Ch1) | 31628
| 31629 | Data(word2) | 2 | Data | Humidity | Humidity | Humidity | 0 | Ch1 Count HO | Ch1 Count HO | 0 | Ch1 Count HO | Temperature (Ch2) | 0 | Humidity | 0 | 0 | Temperature (Ch2) | 31629
| 31630 | Data(word3) | 2 | Data | 0 | VOC | VOC | 0 | Ch1 Count LO | Ch1 Count LO | 0 | Ch1 Count LO | 0 | 0 | 0 | 0 | 0 | 0 | 31630
| 31631 | Data(word4) | 2 | Data | 0 | 0 | CO2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31631
| 31632 | Data(word5) | 2 | Data | 0 | 0 | 0 | 0 | Ch2 Count HO | Ch2 Count HO | 0 | Ch2 Count HO | 0 | 0 | 0 | 0 | 0 | 0 | 31632
| 31633 | Data(word6) | 2 | Data | 0 | 0 | 0 | 0 | Ch2 Count LO | Ch2 Count LO | 0 | Ch2 Count LO | 0 | 0 | 0 | 0 | 0 | 0 | 31633
| 31634 | Data(word7) | 2 | Data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31634
| 31635 | Data(word8) | 2 | Data | 0 | 0 | 0 | 0 | OC Count HO | OC Count HO | OC Count HO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31635
| 31636 | Data(word9) | 2 | Data | 0 | 0 | 0 | 0 | OC Count LO | OC Count LO | OC Count LO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31636
| 31637 | Spare | 2 | Spare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31637
| 31638 | Spare | 2 | Spare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31638
| 31639 | Spare | 2 | Spare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31639
| 31640 | Tx Counter | 2 | Transmission Counter sent by Tx | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | 31640
| 31641 | RSSI | 2 | Received RSSI value | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | 31641
| 31642 | Timer | 2 | Time since last reading value - increments every 1 min and resets when data received | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | 31642
| . |  |  | .
| . |  |  | .
| . |  |  | .
| . |  |  | .
| . |  |  | .
40 | 31783 | DeviceID( Higher word) | 2 | Device ID HO | [14 empty] | 31783 | bar: 0 to 13
| 31784 | DeviceID( Lower word) | 2 | Device ID LO | [14 empty] | 31784 | bar: 0 to 13
| 31785 | Device Type / F/W ver | 2 | Higher Byte Type / Lower Byte Firmware version | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | 31785
| 31786 | Status | 2 | Status (see bit descriptions) | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | 31786
| 31787 | Alarm Status | 2 | Alarm Status (see bit descriptions) | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | 31787
| 31788 | Data(word1) | 2 | Data | Temperature | Temperature | Temperature | Temperature | 0 | 0 | 0 | 0 | Temperature (Ch1) | Analog Value | Temperature | Temperature (Ch1) | Temperature (Ch1) | Temperature (Ch1) | 31788
| 31789 | Data(word2) | 2 | Data | Humidity | Humidity | Humidity | 0 | Ch1 Count HO | Ch1 Count HO | 0 | Ch1 Count HO | Temperature (Ch2) | 0 | Humidity | 0 | 0 | Temperature (Ch2) | 31789
| 31790 | Data(word3) | 2 | Data | 0 | VOC | VOC | 0 | Ch1 Count LO | Ch1 Count LO | 0 | Ch1 Count LO | 0 | 0 | 0 | 0 | 0 | 0 | 31790
| 31791 | Data(word4) | 2 | Data | 0 | 0 | CO2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31791
| 31792 | Data(word5) | 2 | Data | 0 | 0 | 0 | 0 | Ch2 Count HO | Ch2 Count HO | 0 | Ch2 Count HO | 0 | 0 | 0 | 0 | 0 | 0 | 31792
| 31793 | Data(word6) | 2 | Data | 0 | 0 | 0 | 0 | Ch2 Count LO | Ch2 Count LO | 0 | Ch2 Count LO | 0 | 0 | 0 | 0 | 0 | 0 | 31793
| 31794 | Data(word7) | 2 | Data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31794
| 31795 | Data(word8) | 2 | Data | 0 | 0 | 0 | 0 | OC Count HO | OC Count HO | OC Count HO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31795
| 31796 | Data(word9) | 2 | Data | 0 | 0 | 0 | 0 | OC Count LO | OC Count LO | OC Count LO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31796
| 31797 | Spare | 2 | Spare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31797
| 31798 | Spare | 2 | Spare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31798
| 31799 | Spare | 2 | Spare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31799
| 31800 | Tx Counter | 2 | Transmission Counter sent by Tx | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | 31800
| 31801 | RSSI | 2 | Received RSSI value | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | 31801
| 31802 | Timer | 2 | Time since last reading value - increments every 1 min and resets when data received | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | 31802

## Registres de statut
| Enxxx | EN302 | EN303 | EN304 | EN305 | EN308 | EN309 | EN310 | EN319 | EN306 | EN307 | EN311
| Name | Ambient T&H | Ambient T&H / VOC | Ambient T&H / VOC / CO2 | Tx Temp Internal Sensor | Tx Pulse | Tx Pulse (Atex) | Tx Pulse (Fludia) | Tx Contact | Tx Temp Ext PT1000 (2) | Tx Analog 4-20mA | External T&H | Tx Temp Ext PT1000 (1) | Tx Temp Ext PT1000 (1) Ext Power | Tx Temp Ext PT1000 (2) Ext Power
| Enless Ref | TX T&H AMB 600-021 | TX VOC/T&H AMB 600-022 | TX CO2/VOC/T&H AMB 600-023 | TX TEMP INS 600-031 | TX PULSE 600-036 | TX PULSE ATEX 600-037 | TX PULSE LED 600-038 | TX CONTACT 600-039 | TX TEMP CONT2 600-232 | TX 4/20 mA 600-035 | TX T&H 600-034 | TX TEMP CONT1 600-032 | TX TEMP CONT1 MP 600-033 | TX TEMP CONT2 MP 600-233
| Tx Type | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
Bit
Status Register (2 bytes) | 0 | Nor / Alm Msg | Nor / Alm Msg | Nor / Alm Msg | Nor / Alm Msg | Nor / Alm Msg | Nor / Alm Msg | Nor / Alm Msg | Nor / Alm Msg | Nor / Alm Msg | Nor / Alm Msg | Nor / Alm Msg | Nor / Alm Msg | Nor / Alm Msg | Nor / Alm Msg
| 1 | Direct / Rptr Msg | Direct / Rptr Msg | Direct / Rptr Msg | Direct / Rptr Msg | Direct / Rptr Msg | Direct / Rptr Msg | Direct / Rptr Msg | Direct / Rptr Msg | Direct / Rptr Msg | Direct / Rptr Msg | Direct / Rptr Msg | Direct / Rptr Msg | Direct / Rptr Msg | Direct / Rptr Msg
| 2 | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level
| 3 | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level
| 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 0 | 0 | 0 | 0 | Ch1 Status | Ch1 Status | Ch1 Status | Ch1 Status | 0 | 0 | 0 | 0 | 0 | 0
| 6 | 0 | 0 | 0 | 0 | Ch2 Status | Ch2 Status | Ch2 Status | Ch2 Status | 0 | 0 | 0 | 0 | 0 | 0
| 7 | 0 | 0 | 0 | 0 | OC Status | OC Status | OC Status | OC Status | 0 | 0 | 0 | 0 | 0 | 0
| 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bit
Alarm Status Register (2 bytes) | 0 | Temp Hi Alm | Temp Hi Alm | Temp Hi Alm | Temp Hi Alm | Ch1 Flow Alm Hi | Ch1 Flow Alm Hi | Ch1 Flow Alm Hi | Ch1 No Change Alm | Temp1 Hi Alm | Analog Hi Alm | Temp Hi Alm | Temp1 Hi Alm | Temp1 Hi Alm | Temp1 Hi Alm
| 1 | Temp Lo Alm | Temp Lo Alm | Temp Lo Alm | Temp Lo Alm | Ch2 Flow Alm Hi | Ch2 Flow Alm Hi | Ch2 Flow Alm Hi | Ch2 No Change Alm | Temp1 Lo Alm | Analog Lo Alm | Temp Lo Alm | Temp1 Lo Alm | Temp1 Lo Alm | Temp1 Lo Alm
| 2 | Hum Hi Alm | Hum Hi Alm | Hum Hi Alm | 0 | OC Flow Alm HI | OC Flow Alm HI | OC Flow Alm HI | OC No Change Alm | Temp2 Hi Alm | 0 | Hum Hi Alm | 0 | 0 | Temp2 Hi Alm
| 3 | Hum Lo Alm | Hum Lo Alm | Hum Lo Alm | 0 | 0 | 0 | 0 | 0 | Temp2 Lo Alm | 0 | Hum Lo Alm | 0 | 0 | Temp2 Lo Alm
| 4 | 0 | VOC Hi Alm | VOC Hi Alm | 0 | Ch1 Flow Alm Lo | Ch1 Flow Alm Lo | Ch1 Flow Alm Lo | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 0 | VOC lo Alm | VOC lo Alm | 0 | Ch2 Flow Alm Lo | Ch2 Flow Alm Lo | Ch2 Flow Alm Lo | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6 | 0 | 0 | CO2 Hi Alm | 0 | OC Flow Alm Lo | OC Flow Alm Lo | OC Flow Alm Lo | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7 | 0 | 0 | CO2 Lo Alm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8 | 0 | 0 | 0 | 0 | Ch1 Leak Alm | Ch1 Leak Alm | Ch1 Leak Alm | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 9 | 0 | 0 | 0 | 0 | Ch2 Leak Alm | Ch2 Leak Alm | Ch2 Leak Alm | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10 | 0 | 0 | 0 | 0 | OC Leak Alm | OC Leak Alm | OC Leak Alm | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Format des registres
Label | Description | Bits | Hexadecimal | Decimal | TX T&H AMB 600-021 | TX VOC/T&H AMB 600-022 | TX CO2/VOC/T&H AMB 600-023 | TX TEMP INS 600-031 | TX PULSE 600-036 | TX PULSE ATEX 600-037 | TX PULSE LED 600-038 | TX CONTACT 600-039 | TX TEMP CONT2 600-232 | TX 4/20 mA 600-035 | TX T&H 600-034 | TX TEMP CONT1 600-032 | TX TEMP CONT1 MP 600-033 | TX TEMP CONT2 MP 600-233
ID (HO & LO) | Product ID | 32 bit Unsigned Integer | 0x00000000 - 0xFFFFFFFF | 0 - 4294967295 | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓
Type / Ver | HO Byte shows Product Type / LO Byte is Revision Number | 16 bit Unsigned Integer | 0x0000 - 0xFFFF | 0 - 65535 | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓
Status | To be handled Bitwise - see bit descriptions example: 0x2129 = binary 0010 0001 0010 1001 | 16 bit Unsigned Integer | 0x0000 - 0xFFFF | 0 - 65535 | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓
Alarm Status | To be handled Bitwise - see bit descriptions example: 0x2129 = binary 0010 0001 0010 1001 | 16 bit Unsigned Integer | 0x0000 - 0xFFFF | 0 - 65535 | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓
Temperature | If reading Failed, value will be 0x7FFF Temperature = Value / 10 example 0x000FD = 253 dec = 25.3 degC 0xFFD1 = 65489 = -4.7 degC ( 65536 – 65489 ) | 16 bit Signed Integer | 0x0000 - 0xFFFF | 0 - 65535 | ✓ | ✓ | ✓ | ✓ | [6 empty] | ✓
Humidity | If reading Failed, value will be 0xFFFF Humidity = Value / 10 example: 0x0178 = 376 = 37.6% | 16 bit Unsigned Integer | 0x0000 - 0xFFFF | 0 - 65535 | ✓ | ✓ | ✓ | [7 empty] | ✓
VOC | If reading Failed, value will be 0xFFFF VOC = value example: 0x0175 = 373 ppb | 16 bit Unsigned Integer | 0x0000 - 0xFFFF | 0 - 65535 |  | ✓ | ✓
CO2 | If reading Failed, value will be 0xFFFF CO2 = Value example: 0x0189 = 393 ppm | 16 bit Unsigned Integer | 0x0000 - 0xFFFF | 0 - 65535 |  |  | ✓
Temperature (Ch1) | If reading Failed, value will be 0x7FFF Temperature = Value / 10 example 00FD (hex) = 253 dec = 25.3 degC FFD1 (hex) = 65489 = -4.7 degC ( 65536 – 65489 ) | 16 bit Signed Integer | 0x0000 - 0xFFFF | 0 - 65535 | [8 empty] | ✓ |  |  | ✓ | ✓ | ✓
Temperature (Ch2) | If reading Failed, value will be 0x7FFF Temperature = Value / 10 example 00FD (hex) = 253 dec = 25.3 degC FFD1 (hex) = 65489 = -4.7 degC ( 65536 – 65489 ) | 16 bit Signed Integer | 0x0000 - 0xFFFF | 0 - 65535 | [8 empty] | ✓ |  |  |  |  | ✓
Analog Value | Current in microamps mA = Value / 1000 example: 0x1020 = 4128 = 4.128mA | 16 bit Unsigned Integer | 0x0000 - 0xFFFF | 0 - 65535 | [9 empty] | ✓
Ch1 Count HO & LO | Pulse Count = 32 bit value example: 0x0001 0203 = 66051 | 32 bit Unsigned Integer | 0x00000000 - 0xFFFFFFFF | 0 - 4294967295 |  |  |  |  | ✓ | ✓ |  | ✓
Ch2 Count HO & LO | Pulse Count = 32 bit value example: 0x0001 0203 = 66051 | 32 bit Unsigned Integer | 0x00000000 - 0xFFFFFFFF | 0 - 4294967295 |  |  |  |  | ✓ | ✓ |  | ✓
OC Count HO & LO | Pulse Count = 32 bit value example: 0x0001 0203 = 66051 | 32 bit Unsigned Integer | 0x00000000 - 0xFFFFFFFF | 0 - 4294967295 |  |  |  |  | ✓ | ✓ | ✓
Tx Count | Count = Value example: 0x001B = 27 | 16 bit Unsigned Integer | 0x0000 - 0xFFFF | 0 - 65535 | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓
Received RSSI | RSSI = Value example: 0xFFDA = -38dbm | 16 bit Signed Integer | 0x0000 - 0xFFFF | 0 - 65535 | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓
Timer (mins) | Timer = Value example: 0x0005 = 5min | 16 bit Unsigned Integer | 0x0000 - 0xFFFF | 0 - 65535 | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓

## Registres de configuration
| 45000 | First Register
[5 empty] | Enxxx | EN302 | EN303 | EN304 | EN305 | EN308 | EN309 | EN310 | EN319 | EN306 | EN307 | EN311
| Modbus Register Table for Transmitters Configuration (Read / Write) |  |  |  | Name | Ambient T&H | Ambient T&H / VOC | Ambient T&H / VOC / CO2 | Tx Temp Internal Sensor | Tx Pulse | Tx Pulse (Atex) | Tx Pulse (Fludia) | Tx Contact | Tx Temp Ext PT1000 (2) | Tx Analog 4-20mA | External T&H | Tx Temp Ext PT1000 (1) | Tx Temp Ext PT1000 (1) Ext Power | Tx Temp Ext PT1000 (2) Ext Power
[5 empty] | Enless Ref | TX T&H AMB 600-021 | TX VOC/T&H AMB 600-022 | TX CO2/VOC/T&H AMB 600-023 | TX TEMP INS 600-031 | TX PULSE 600-036 | TX PULSE ATEX 600-037 | TX PULSE LED 600-038 | TX CONTACT 600-039 | TX TEMP CONT2 600-232 | TX 4/20 mA 600-035 | TX T&H 600-034 | TX TEMP CONT1 600-032 | TX TEMP CONT1 MP 600-033 | TX TEMP CONT2 MP 600-233
[5 empty] | Tx Type | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
| Register Address | Parameter | Bytes | Comment
| 45000 | Spare | 2 | Spare
| 45001 | Spare | 2 | Spare
| 45002 | Spare | 2 | Spare
25 | 45963 | DeviceID( Higher word) | 2 | Device ID HO | bar: 0 to 13
| 45964 | DeviceID( Lower word) | 2 | Device ID LO | bar: 0 to 13
| 45965 | Tx Period | 2 | Transmission Period in mins |  | Tx Period (5min) | Tx Period (15min) | Tx Period (15min) | Tx Period (5min) | Tx Period (5min) | Tx Period (5min) | Tx Period (5min) | Tx Period (5min) | Tx Period (5min) | Tx Period (5min) | Tx Period (5min) | Tx Period (5min) | Tx Period (5min) | Tx Period (5min)
| 45966 | TWU Period | 2 | Time windown Upgrade Time in mins |  | TWU Period (0) | TWU Period (0) | TWU Period (0) | TWU Period (0) | TWU Period (0) | TWU Period (0) | TWU Period (0) | TWU Period (0) | TWU Period (0) | TWU Period (0) | TWU Period (0) | TWU Period (0) | TWU Period (0) | TWU Period (0)
| 45967 | Alarm Threshold Period | 2 | Alarm Threshold Period in Secs (time before alarm is sent) |  | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero
| 45968 | Tx Type | 2 | Transmitter Type |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
| 45969 | Alarm Setting | 2 | Alarm Setting |  | Temp Hi - P1 (0) | Temp Hi - P1 (0) | Temp Hi - P1 (0) | Temp Hi - P1 (0) | Ch1 Flow Hi - P1 (0) | Ch1 Flow Hi - P1 (0) | zero | Ch1 Input Period - P1 (0) | Temp1 Hi - P1 (0) | Analog Hi - P1 (0) | Temp1 Hi - P1 (0) | Temp1 Hi - P1 (0) | Temp1 Hi - P1 (0) | Temp1 Hi - P1 (0)
| 45970 | Alarm Setting | 2 | Alarm Setting |  | Temp Lo - P2 (0) | Temp Lo - P2 (0) | Temp Lo - P2 (0) | Temp Lo - P2 (0) | Ch1 Flow Lo - P2 (0) | Ch1 Flow Lo - P2 (0) | zero | Ch2 Input Period - P2 (0) | Temp1 Lo - P2 (0) | Analog Lo - P2 (0) | Temp1 Lo - P2 (0) | Temp1 Lo - P2 (0) | Temp1 Lo - P2 (0) | Temp1 Lo - P2 (0)
| 45971 | Alarm Setting | 2 | Alarm Setting |  | Hum Hi - P3 (0) | Hum Hi - P3 (0) | Hum Hi - P3 (0) | zero | Ch1 Flow Time - P3 (0) | Ch1 Flow Time - P3 (0) | zero | zero | Temp2 Hi - P3 (0) | Loop Period - P3 (0) | Hum Hi - P3 (0) | zero | zero | Temp2 Hi - P3 (0)
| 45972 | Alarm Setting | 2 | Alarm Setting |  | Hum Lo - P4 (0) | Hum Lo - P4 (0) | Hum Lo - P4 (0) | zero | Ch1 Leak Threshold - P4 (0) | Ch1 Leak Threshold - P4 (0) | zero | zero | Temp2 Lo - P4 (0) | zero | Hum Lo - P4 (0) | zero | zero | Temp2 Lo - P4 (0)
| 45973 | Alarm Setting | 2 | Alarm Setting |  | zero | VOC Hi - P5 (0) | VOC Hi - P5 (0) | zero | Ch2 Flow Hi - P5 (0) | Ch2 Flow Hi - P5 (0) | zero | zero | zero | zero | zero | zero | zero | zero
| 45974 | Alarm Setting | 2 | Alarm Setting |  | zero | VOC Lo - P6 (0) | VOC Lo - P6 (0) | zero | Ch2 Flow Lo - P6 (0) | Ch2 Flow Lo - P6 (0) | zero | zero | zero | zero | zero | zero | zero | zero
| 45975 | Alarm Setting | 2 | Alarm Setting |  | zero | zero | CO2 Hi - P7 (0) | zero | Ch2 Flow Time - P7 (0) | Ch2 Flow Time - P7 (0) | zero | zero | zero | zero | zero | zero | zero | zero
| 45976 | Alarm Setting | 2 | Alarm Setting |  | zero | zero | CO2 Lo - P8 (0) | zero | Ch2 Leak Threshold - P8 (0) | Ch2 Leak Threshold - P8 (0) | zero | zero | zero | zero | zero | zero | zero | zero
| 45977 | Alarm Setting | 2 | Alarm Setting |  | zero | zero | zero | zero | OC Flow Hi - P9 (0) | OC Flow Hi - P9 (0) | OC Flow Hi - P9 (0) | zero | zero | zero | zero | zero | zero | zero
| 45978 | Alarm Setting | 2 | Alarm Setting |  | zero | zero | zero | zero | OC Flow Lo - P10 (0) | OC Flow Lo - P10 (0) | OC Flow Lo - P10 (0) | zero | zero | zero | zero | zero | zero | zero
| 45979 | Alarm Setting | 2 | Alarm Setting |  | zero | zero | zero | zero | OC Flow Time - P11 (0) | OC Flow Time - P11 (0) | OC Flow Time - P11 (0) | zero | zero | zero | zero | zero | zero | zero
| 45980 | Alarm Setting | 2 | Alarm Setting |  | zero | zero | zero | zero | OC Leak Threshold - P12 (0) | OC Leak Threshold - P12 (0) | OC Leak Threshold - P12 (0) | zero | zero | zero | zero | zero | zero | zero
| 45981 | Spare | 2 | Spare |  | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero
| 45982 | Spare | 2 | Spare |  | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero
| 45983 | Spare | 2 | Spare |  | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero
| 45984 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45985 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45986 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45987 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45988 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45989 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45990 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45991 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45992 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45993 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45994 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45995 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45996 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45997 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45998 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45999 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 46000 | Spare | 2 | Spare |  | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero
| 46001 | Spare | 2 | Spare |  | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero
| 46002 | Spare | 2 | Spare |  | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero